## Sheet1
Installation of plastic pipes
Thermal expansion in plastics
There are two factors to consider when calculating expansion or contraction in pipes: -
• Environmental temperature (external temperature) at which the pipe will stabilise prior to installation.
• Fluid temperature (internal temperature) which is the operational temperature of the pipeline system.
The change in length due to thermal expansion or contraction in a pipeline system is determined by the following formula:
Where | ΔL Expansion (ΔLe) or contraction (ΔLc) in mm
ΔT Difference in temperature between the
installation and the operating
temperatures in °C (=T operate - T install)
L Length of pipe when installed
δ Coefficient of expansion
Diameter | 50
Length | 5
Install temperature | 10
Operating temp | 20
|  | Length/temperature equivalent (mm/m°C) | Cm
Material | PVC | 0.078 | 33.5
Material | Coefficient δ (10-5m/m°C) | Length/temperature equivalent (mm/m°C) | Cm
PVC | 7.8 | 0.078 | 33.5
ABS | 10.1 | 0.101 | 32.7
PP | 15 | 0.15 | 30
PE100 | 20 | 0.2 | 26
Expansion or contraction | 3.9
3.9
How to find the flexible arm (a) length
To calculate the length of a fl exible arm () the following
formulae can be used: -
Single arm:
Double arm:
Where a Flexible arm length (mm)
D Pipe outside diameter (mm)
ΔL Expansion or Contraction (mm) for single
arm, for double arm use ΔL/2
Cm Constant for material, see table 6.3
Single arm | 467.802
Double arm | 330.786
Figure 1 single arm | Figure 2 double arm (expansion loop)
www.polypipe.com/effast

## Sheet2
| Cm | PVCu | 33.5
|  | ABS | 32.7 | 32.7
|  | PP | 30
|  | PE | 26
|  | Diameter | 40
Single arm | 408.4229
Double arm | 288.7986